## Slide 1
PV101 DAY 5
Commissioning, Protection
& Fault Finding
Monday, July 13, 2026 | CTS Cohort 6
PV
Controller
Battery
Fuse
Load
Verify the path before you energize it.

## Slide 2
Today’s job
Use yesterday’s completed build as a system to inspect, prove, protect, and troubleshoot.
CTS Cohort 6 | PV101 Day 5 | 2026-07-13
Power path
Protection
Measurement
Serviceability
Students must identify where current can come from.
Fuses protect wires from too much current.
Every important claim gets verified with a meter.
The final build should make sense to a tired future technician.

## Slide 3
The four numbers
A small system is easier when students can translate the electrical language.
CTS Cohort 6 | PV101 Day 5 | 2026-07-13
Voltage
V
Electrical pressure
Current
A
Flow of charge
Power
W
Work being done
Resistance
Ω
Opposition to flow
Power formula: P = V × A
Example: 12.8 V × 5 A = 64 W

## Slide 4
Series vs. parallel
Ask students to predict first, then prove it.
CTS Cohort 6 | PV101 Day 5 | 2026-07-13
Series: voltage adds
12 V
12 V
24 V path
Same path for current
One weak part affects the whole string
Parallel: voltage stays, current capacity increases
12 V
12 V
12 V bus
more available current
Classroom sentence: series changes voltage, parallel keeps voltage common.

## Slide 5
Fuse logic
A fuse protects the conductor from the source. It is not a magic device shield.
CTS Cohort 6 | PV101 Day 5 | 2026-07-13
Battery
source
Fuse
near +
Wire run
Inverter
or load
If the wire shorts before the fuse, the fuse cannot help. Humanity learns this repeatedly.
Place the fuse close to battery positive.
Fuse size must match the wire and expected load.
Stop and inspect if heat, smell, sparks, or weird readings appear.

## Slide 6
Wire sizing and voltage drop
The wire is part of the system, not just a thing that connects the system.
CTS Cohort 6 | PV101 Day 5 | 2026-07-13
More current
Longer run
Smaller wire
More voltage drop
Voltage drop test
Measure voltage at battery under load.
Measure voltage at load/inverter under load.
Subtract: battery-end minus load-end.
High drop means resistance, undersized wire, bad crimp, loose terminal, or too much current.
Never “fix” voltage drop by just turning things up. Find the cause.

## Slide 7
RV solar power path
Students should be able to draw this before touching wires.
CTS Cohort 6 | PV101 Day 5 | 2026-07-13
PV panel
Charge
controller
LiFePO4
battery
Fuse /
breaker
Inverter
/ loads
Inspection questions
Where can current come from?
What protects each wire?
What readings prove polarity and voltage?
What would you label for service later?
Order matters
Controller to battery first unless manual says otherwise.
PV last. Loads after inspection.
Unexpected readings mean stop and trace.

## Slide 8
Afternoon lab: commission, then diagnose
Keep Day 4 systems assembled. Rotate through inspection, measurement, fault evidence, and restoration.
CTS Cohort 6 | PV101 Day 5 | 2026-07-13
Lead inspector
Meter lead
Recorder / verifier
Traces path
Checks protection
Improves labels
Predicts readings
Measures safely
Checks voltage drop
Records evidence
Controls sequence
Verifies restoration
No rebuilding unless a measured fault requires a correction. One change at a time.

## Slide 9
Commissioning and troubleshooting flow
No random touching. Observe, predict, measure, act. Wild concept, apparently.
CTS Cohort 6 | PV101 Day 5 | 2026-07-13
Observe
What changed?
Predict
What reading should exist?
Measure
Use the meter correctly
Act
Change one thing
Verify
Did the evidence improve?
Wrong polarity? Stop before energizing.
No output? Check source, fuse, wiring path, and controller state.
Low voltage under load? Check current, wire size, crimps, and voltage drop.
Heat, smell, spark, or weird reading? Hands off, call instructor.

## Slide 10
Exit ticket
Three things every student should leave with.
CTS Cohort 6 | PV101 Day 5 | 2026-07-13
I can verify with a meter...
A fuse protects...
A fault I can now diagnose systematically...
Cleanup standard
Every kit restored and verified.
Tools back. No mystery wires.
Labels improved for the next technician.
Instructor close
The win is not rebuilding yesterday’s work. The win is proving it, diagnosing it, and returning it to known-good condition.