# PV101 Day 7 Student Worksheet Answer Key

Instructor copy

Day_07_PV101_Load_Assessment_and_System_Sizing_2026-07-15

# RV training loads

| Load | Calculation | Wh/day |
| --- | --- | --- |
| 3 interior LED lights | 3 x 8 W x 4 h | 96 |
| Water pump | 60 W x 0.5 h | 30 |
| Vent fan | 36 W x 3 h | 108 |
| Phone/USB charging | 24 W x 2 h | 48 |
| Laptop charger (AC) | 65 W x 2 h | 130 |
| Total | 96 + 30 + 108 + 48 + 130 | 412 Wh/day |

# Storage

Required stored energy: 412 Wh/day x 1 day = 412 Wh.

Battery nameplate energy: 412 Wh / 0.80 = 515 Wh.

Basic capacity at 12 V: 515 Wh / 12 V = 42.9 Ah.

Accept clear rounding. Students must state the 1-day autonomy and 80% usable-fraction / maximum-depth-of-discharge assumptions.

# Array and inverter

Raw array watts: 412 Wh / 4 peak sun hours = 103 W.

Adjusted exercise result: 103 W x 1.25 = 128.75 W, or about 129 W.

Concurrent AC load: 65 W for the laptop charger; the other listed loads are treated as DC in this exercise.

Minimum inverter exercise result: 65 W x 1.25 = 81.25 W.

Do not turn the result into a product recommendation. Actual selection needs real specifications, surge data, and documented design inputs.

# One-line diagram acceptance

Accept a clearly labeled path such as PV -> charge controller -> battery -> protected DC load/inverter branches. Require complete return paths, source-side protection, disconnects, polarity/labels, and logical meter points. Conceptual variants are acceptable when electrically coherent and safely explained.