## Slide 1
CTS Cohort 6 | RCS03 | Day 11 | July 22, 2026
RCS Day 3
Receptacle boxes, conductor paths, terminations, and de-energized checks
DE-ENERGIZE. TRACE. TERMINATE. VERIFY.
Training mock-ups only. No connection to building power. Every circuit stays isolated.
Today the goal is not to make power. The goal is a safe, inspectable wiring path.
1
Notes: Open with the corrected lab mission. All kits remain disconnected until approval.

## Slide 2
CTS Cohort 6 | RCS03 | Day 11 | July 22, 2026
Today's flow
Quiz -> model -> guided practice -> capstone lab -> QC
Quiz
10:15
Circuit path
10:50
Box demo
11:20
QC ladder
12:00
Build
1:00
Verify
2:25
Exit
2:45
Morning: trace hot, neutral, and equipment-grounding paths.
Afternoon: mount two boxes and terminate two training receptacles.
End: visual check, tug check, continuity, label, photo, reset.
2
Notes: Use this to keep Rich and students oriented.

## Slide 3
CTS Cohort 6 | RCS03 | Day 11 | July 22, 2026
Today's targets
What successful work must demonstrate
Hot
path out
Neutral
path back
Grounding
fault path
Device
boxes
Receptacles
+ evidence
Trace hot, neutral, and equipment-grounding paths in a training circuit
Lay out two receptacle boxes on the capstone wall
Prepare and terminate conductors on training receptacles
Complete visual, mechanical, and continuity checks while de-energized
3
Notes: Emphasize the inverter is not a tiny controller load.

## Slide 4
CTS Cohort 6 | RCS03 | Day 11 | July 22, 2026
The day's path
Trace the work before building it
Source
isolated
Protection
identified
Hot to
device
Neutral
return
Ground +
document
Trace the expected circuit before routing cable. Every student calls the energy state before touching a conductor.
4
Notes: Ask students to point out positive and negative paths.

## Slide 5
CTS Cohort 6 | RCS03 | Day 11 | July 22, 2026
Controlled sequence
Release each stage only after its check
1
Verify isolation
2
Lay out + mount boxes
3
Route + terminate
4
Inspect + continuity
Instructor approves both box locations before drilling. No student test begins until isolation is verified.
5
Notes: Say “most controllers” because manuals vary. Teach general practice plus verify equipment.

## Slide 6
CTS Cohort 6 | RCS03 | Day 11 | July 22, 2026
Working roles
6 students; every result receives another set of eyes
Builder
routes + terminates
Inspector
visual + tug check
Documenter
logs + photographs
Rotate at the first completed receptacle.
The Inspector checks jacket entry, insulation, copper, and terminal security.
The instructor controls any test source.
6
Notes: This matches the actual five-kit/six-student constraint.

## Slide 7
CTS Cohort 6 | RCS03 | Day 11 | July 22, 2026
Verification checkpoints
Do not trust appearance alone
Isolation proven
Visual inspection
Mechanical tug
Continuity check
Use continuity only on an isolated circuit.
Expected path first; meter setup second; reading third.
A continuity result does not authorize energized operation.
7
Notes: Have students practice the measurement sentence.

## Slide 8
CTS Cohort 6 | RCS03 | Day 11 | July 22, 2026
Safety boundaries
The lab begins only inside these controls
No building power
Treat unknown as live
Eyes for drilling
Instructor test control
Keep the mock-up de-energized and separate from premises wiring. Stop for damaged insulation, exposed loose copper, or an unverified energy state.
8
Notes: Do not overdo calculations today. Keep the principle concrete.

## Slide 9
CTS Cohort 6 | RCS03 | Day 11 | July 22, 2026
Professional judgment
Safe work pauses when the evidence conflicts
Good path
isolate -> trace -> terminate -> check
Bad habit
color guess -> connect -> hope
A professional proves the source state and conductor path. Course practice does not authorize unlicensed field electrical work.
9
Notes: Unless the equipment manual says otherwise, teach inverter battery-side with protection.

## Slide 10
CTS Cohort 6 | RCS03 | Day 11 | July 22, 2026
Quality criteria
Good physical work leaves visible proof
Mount boxes at the approved layout marks.
Protect cable and bring jacket into the box.
Strip without damaging conductor.
Keep loose copper out of the enclosure.
Visual, tug, continuity, and instructor approval.
Unknown energy state? Stop and verify.
10
Notes: Make rework normal. Bad crimps are data. Hidden bad crimps are future pain.

## Slide 11
CTS Cohort 6 | RCS03 | Day 11 | July 22, 2026
Lab release checklist
The station earns work only after the checks
Training source isolated and identified.
Box measurements recorded.
Drilling layout approved.
Conductors match the training diagram.
Continuity mode used only while isolated.
No connection to premises wiring.
11
Notes: Use this slide as the afternoon pass standard.

## Slide 12
CTS Cohort 6 | RCS03 | Day 11 | July 22, 2026
Afternoon lab
Slow sequence. Clear callouts. No surprises.
1
Isolate + lay out
2
Mount + route
3
Terminate two devices
4
Inspect + document
Complete two de-energized receptacle terminations on the capstone wall. Instructor approval is the final checkpoint.
12
Notes: Keep control of the final power-up moment.

## Slide 13
CTS Cohort 6 | RCS03 | Day 11 | July 22, 2026
Closeout order
End verified, documented, and reset
1
Visual inspection
2
Tug test
3
Continuity check
4
Label + close
Record expected and observed results. Leave no exposed conductor, unidentified cable, or energized mystery circuit.
13
Notes: Use this before cleanup so the room ends clean.

## Slide 14
CTS Cohort 6 | RCS03 | Day 11 | July 22, 2026
Evidence log
What students write down
Source
isolated + tagged
Initials: ______
Box 1
layout + secure
Measure: _____
Box 2
layout + secure
Measure: _____
Visual
copper + insulation
Pass: ________
Tug
secure terminals
Pass: ________
Continuity
expected path
Result: _______
No verified isolation, no meter use. No complete QC, no lab approval.
14
Notes: Match the worksheet measurement log.

## Slide 15
CTS Cohort 6 | RCS03 | Day 11 | July 22, 2026
Exit ticket
Three checks before dismissal
1. Trace hot, neutral, and equipment-grounding paths.
2. Name the four verification stages used today.
3. State the boundary for continuity testing.
Mock-up isolated. Devices checked. Conductors labeled. Evidence saved.
15
Notes: Collect tickets and use them to decide what Day 5 needs.