## Slide 1
CTS Cohort 6 | PV101 | Day 7 | July 15, 2026
PV101 Day 7
Chapters 11-12 + guided load assessment and system sizing
LOADS DRIVE SIZING.
Today is guided class practice. Show the math, units, assumptions, one-line path, and verification checks.
Measure. Verify. Document. Then proceed.
1
Notes: Open with the bounded Day 7 purpose. This is not a project or product proposal.

## Slide 2
CTS Cohort 6 | PV101 | Day 7 | July 15, 2026
Today's flow
Quiz -> correction -> worked examples -> guided worksheet -> evidence
Arrival
10:00
Quiz
10:20
Review
10:35
Worked math
11:30
Guided practice
12:00
Worksheet
1:15
Cleanup
2:55
2
Morning: finish the reading sequence with Chapters 11-12.
Midday: connect the full PV101 progression to documented loads.
Afternoon: calculate, diagram, peer-check, revise, and obtain signoff.
Notes: Keep schedule visible; lunch is 12:30-1:00.

## Slide 3
CTS Cohort 6 | PV101 | Day 7 | July 15, 2026
Chapter 11: work inside local requirements
Incentives, resources, permitting, and AHJs
Current official source
AHJ + utility requirements
Permit + review path
Document approvals
Verify incentives with a current authoritative source; programs and eligibility can change.
Identify the local AHJ and serving utility before assuming the approval process.
Permits and inspections belong to safe, documented work.
3
Notes: Correct the Chapter 11 quiz items without turning this into a certification unit.

## Slide 4
CTS Cohort 6 | PV101 | Day 7 | July 15, 2026
Chapter 12: practice with purpose
A score is a result. A reviewed mistake is instruction.
Read the question
Mark units + givens
Solve / select safely
Review the miss
Keep units attached to every value.
If two answers appear possible, prioritize safety and documented procedure.
Check whether the result is reasonable before moving on.
4
Notes: Frame Chapter 12 as cumulative question practice, not certification preparation.

## Slide 5
CTS Cohort 6 | PV101 | Day 7 | July 15, 2026
The sizing chain
Every later choice starts with documented loads
Loads
W + h/day
Energy
Wh/day
Storage
Wh -> Ah
Array
PSH + loss
Inverter
concurrent W
One-line
protect + verify
Do not choose equipment first and invent the load story later.
5
Notes: Ask students to name what evidence feeds each arrow.

## Slide 6
CTS Cohort 6 | PV101 | Day 7 | July 15, 2026
Worked example: daily energy
Watts x hours = watt-hours
3 lights
3 x 8 W x 4 h
= 96 Wh
Pump
60 W x 0.5 h
= 30 Wh
Vent fan
36 W x 3 h
= 108 Wh
Phone + laptop
48 + 130
= 178 Wh
Daily total = 96 + 30 + 108 + 48 + 130 = 412 Wh/day
Check: every load has power, time, multiplication, and an energy unit.
6
Notes: Pause before revealing the total; have students call out each unit.

## Slide 7
CTS Cohort 6 | PV101 | Day 7 | July 15, 2026
Worked example: storage
Use the exercise assumptions exactly as documented
Required stored energy
412 Wh/day x 1 day
= 412 Wh
Nameplate energy
412 Wh / 0.80
= 515 Wh
Basic capacity
515 Wh / 12 V
= 42.9 Ah
Autonomy: 1 day.
Usable fraction / maximum depth of discharge for this exercise: 80%.
System voltage: 12 V.
Round clearly; do not hide the assumption.
7
Notes: These are bounded training assumptions, not product recommendations.

## Slide 8
CTS Cohort 6 | PV101 | Day 7 | July 15, 2026
Worked example: array watts
Document peak sun hours and the loss multiplier
Raw array watts
412 Wh / 4 h
= 103 W
Adjusted array watts
103 W x 1.25
= 128.75 W
Report clearly
about 129 W
minimum exercise result
Peak sun hours are an input. If the input changes, the answer changes.
8
Notes: Do not imply an actual array can be selected without real specifications and site data.

## Slide 9
CTS Cohort 6 | PV101 | Day 7 | July 15, 2026
Inverter sizing starts with power
Daily energy is not the same as simultaneous load
Concurrent AC load
Laptop charger = 65 W
Add exercise headroom
65 W x 1.25
Minimum exercise rating
81.25 W
List the AC loads that can operate at the same time.
Document surge information when a load has a starting surge.
Select from real product ratings only after actual specifications are available.
9
Notes: This worksheet has only one AC load; keep the distinction between W and Wh explicit.

## Slide 10
CTS Cohort 6 | PV101 | Day 7 | July 15, 2026
One-line system path
Show energy flow, return paths, protection, and test points
PV array
Controller
Battery
Fuse + disconnect
Inverter / loads
Mark polarity and the complete return path.
Place protection so it protects the conductor near the source.
Add labels and logical meter points.
Today the diagram is conceptual and must use the provided training assumptions.
10
Notes: Students draw their own diagram; no physical wiring today.

## Slide 11
CTS Cohort 6 | PV101 | Day 7 | July 15, 2026
Instructor checkpoints
A correct answer must also be inspectable
1
Loads + hours
Show units + assumptions
2
Daily Wh
Show units + assumptions
3
Storage Wh/Ah
Show units + assumptions
4
Array + inverter
Show units + assumptions
5
One-line diagram
Show units + assumptions
6
Peer check + signoff
Revise before signature
11
Notes: A substitute should pause the room at each checkpoint.

## Slide 12
CTS Cohort 6 | PV101 | Day 7 | July 15, 2026
Verification check
Before instructor signoff
Loads and hours copied correctly.
Every calculation shows the formula and unit.
Autonomy, usable fraction / depth of discharge, peak sun hours, and loss multiplier match the worksheet.
Answers are reasonable and rounded clearly.
Diagram shows protection, disconnects, labels, meter points, and return path.
Peer check completed and corrections visible.
12
Notes: Do not sign incomplete work. Return it for correction.

## Slide 13
CTS Cohort 6 | PV101 | Day 7 | July 15, 2026
Day 7 closeout
Reflection, evidence, cleanup, final reminder
Submit
worksheet + reflection
Return
calculators + rulers
Leave
tables clear
Tomorrow: cumulative review and a 25-question final assessment.
Cleanup begins at 2:55. Dismissal follows the room reset.
13
Notes: End exactly with evidence collection and cleanup.