## Slide 1
CTS Cohort 6 | PV101 | Day 4 | July 9, 2026
PV101 Day 4
Small solar system build: panel, controller, 12.8V LiFePO4 battery, wiring, inverter
VERIFY FIRST. CONNECT SECOND.
5 kits. 6 students. One shared station. Every build gets peer-checked before power.
Today the goal is not “make the inverter light up.” The goal is a safe, traceable system.
1
Notes: Open with the corrected lab mission. All kits remain disconnected until approval.

## Slide 2
CTS Cohort 6 | PV101 | Day 4 | July 9, 2026
Today's flow
Quiz -> system pieces -> wiring sequence -> kit build
Quiz
10:20
System map
10:55
Demo
11:20
Kit roles
12:30
Build
12:45
Commission
2:20
Exit
2:40
Morning: make the system understandable before anyone touches a conductor.
Afternoon: build five small systems with one two-student shared kit.
End: every kit is shut down, measured, documented, and returned safely.
2
Notes: Use this to keep Rich and students oriented.

## Slide 3
CTS Cohort 6 | PV101 | Day 4 | July 9, 2026
The kit parts
Each station builds one small solar system
PV panel
source
Charge
controller
12.8V LiFePO4
50Ah battery
Fuse /
disconnect
Inverter
DC -> AC
One PV panel feeds the charge controller.
The battery stores energy and stabilizes the system.
The inverter draws from the battery side through protection.
Labels and meter readings make the system serviceable.
3
Notes: Emphasize the inverter is not a tiny controller load.

## Slide 4
CTS Cohort 6 | PV101 | Day 4 | July 9, 2026
System path
Trace it before building it
Sunlight
+ PV panel
Charge
controller
Battery
12.8V 50Ah
Protection
fuse/disconnect
Inverter
AC output
Every positive path needs a matching return path. Every power path needs a safe way to stop.
4
Notes: Ask students to point out positive and negative paths.

## Slide 5
CTS Cohort 6 | PV101 | Day 4 | July 9, 2026
Connection order
Most controllers want battery first, then PV
1
Battery to controller
BAT + / -
2
Meter battery side
~12.8V nominal
3
PV to controller
PV + / -
4
Inverter to battery side
through protection
Keep the PV panel covered or disconnected while wiring.
Keep the battery fuse open/removed until approval.
When unsure, stop. Solar equipment is not impressed by confidence.
5
Notes: Say “most controllers” because manuals vary. Teach general practice plus verify equipment.

## Slide 6
CTS Cohort 6 | PV101 | Day 4 | July 9, 2026
Station roles
5 kits for 6 students
Stations 1-4
solo builder
Station 5
2-student shared kit
All stations
peer-check before power
Two-student station swaps Builder and Inspector roles halfway through.
Solo builders call over a neighbor for peer-check before energizing.
Nobody approves their own mystery wiring. Civilization has suffered enough.
6
Notes: This matches the actual five-kit/six-student constraint.

## Slide 7
CTS Cohort 6 | PV101 | Day 4 | July 9, 2026
Polarity check
Do not trust colors alone
Battery + / -
Controller BAT + / -
Controller PV + / -
Inverter + / -
Call the meter setup: DC volts, correct lead ports, expected range.
Say the reading and probe placement out loud.
A reversed connection can damage controller or inverter hardware.
7
Notes: Have students practice the measurement sentence.

## Slide 8
CTS Cohort 6 | PV101 | Day 4 | July 9, 2026
Protection matters
A 50Ah battery is not a toy just because it fits on a bench
Fuse close to battery
Correct conductor path
Visible disconnect
No loose copper
Protection exists to protect conductors and equipment from fault current.
Put protection where it protects the most wire.
Open/remove protection before changing wiring.
8
Notes: Do not overdo calculations today. Keep the principle concrete.

## Slide 9
CTS Cohort 6 | PV101 | Day 4 | July 9, 2026
Inverter rule
The inverter belongs on the battery side through protection
Good path
Battery -> fuse -> inverter
Bad habit
Controller load terminals -> inverter
Inverters can draw high current. Controller load terminals are often for small DC loads, not “whatever fits.”
9
Notes: Unless the equipment manual says otherwise, teach inverter battery-side with protection.

## Slide 10
CTS Cohort 6 | PV101 | Day 4 | July 9, 2026
Mechanical quality
Good electrical work starts as good physical work
Strip without nicking strands.
Use the correct crimp die and complete the ratchet cycle.
Tug test every crimp.
Route wires so terminals are not holding mechanical strain.
Leave enough slack for service, but not a spaghetti shrine.
Bad crimp? Cut it off and redo it.
10
Notes: Make rework normal. Bad crimps are data. Hidden bad crimps are future pain.

## Slide 11
CTS Cohort 6 | PV101 | Day 4 | July 9, 2026
Commissioning checklist
A kit earns power only after the checks
PV covered or disconnected during wiring.
Battery fuse/breaker open until approval.
Battery voltage measured directly and at controller.
PV polarity and voltage measured before final connection.
Inverter input path traced and protected.
Peer check complete, then instructor approval.
11
Notes: Use this slide as the afternoon pass standard.

## Slide 12
CTS Cohort 6 | PV101 | Day 4 | July 9, 2026
Energizing order
Slow sequence. Clear callouts. No surprises.
1
Close battery protection
2
Controller wakes up
3
Uncover/connect PV
4
Turn inverter on
Test only with an approved small load. No creative experiments. This is class, not a mythology generator.
12
Notes: Keep control of the final power-up moment.

## Slide 13
CTS Cohort 6 | PV101 | Day 4 | July 9, 2026
Shutdown order
End safe, not merely “done”
1
Inverter off
2
Cover/disconnect PV
3
Open battery protection
4
Document + clean kit
Record readings before forgetting them, the classic human speedrun.
Return all kit parts together.
Leave no energized mystery wiring.
13
Notes: Use this before cleanup so the room ends clean.

## Slide 14
CTS Cohort 6 | PV101 | Day 4 | July 9, 2026
Measurement log
What students write down
Battery direct
VDC + polarity
Measured: ________
Controller BAT
VDC + polarity
Measured: ________
PV open circuit
VDC + polarity
Measured: ________
Controller PV
VDC + polarity
Measured: ________
Inverter input
VDC + protection
Measured: ________
AC output
approved load only
Measured: ________
No measurement, no approval. The electrons can wait.
14
Notes: Match the worksheet measurement log.

## Slide 15
CTS Cohort 6 | PV101 | Day 4 | July 9, 2026
Exit ticket
Three checks before dismissal
1. Trace: PV -> controller -> battery -> inverter -> load.
2. What connects first on most controllers: battery or PV? Why?
3. Name one STOP condition from today's lab.
Tools counted. Kits safe. Panels covered. Batteries protected.
15
Notes: Collect tickets and use them to decide what Day 5 needs.